## Sheet1
Equipment | Task ID | Task Name | Interval Type | Interval Value | Interval Unit | Trigger Context | Tracking Mode | Hours Source | Calendar Rule | Due Threshold (days) | Document Name | Document File/Link | Manual Page | Procedure Summary | Safety/Notes | Owner | Last Done Date | Last Done Hours | Last Done Furnace Hours | Last_Done_Draw | Required Parts | Group | Planning months | Estimated duration min | Last_Done_Hours_UV1 | Last_Done_Hours_UV2 | Last_Done_Hours_Furnace
Clean Air System (HEPA + Pre-filter + Fan Cabinet) | CAS-MNT-001 | Before drawing: ensure intake air temp matches tower environment; check clean air velocity (0.25–0.5 m/s) | run | 1 | before fibre drawing operations | Operation – before commencing drawing | event |  |  |  | Clean Air System (SG Controls) | Clean Air System.pdf | 3 | 1) Ensure the air drawn into the pre-filter cabinet is at the same temperature as the tower environment to prevent condensation / convection effects. 2) Check airflow from HEPA filters is at a predetermined value within 0.25–0.5 m/s using an anemometer; adjust airflow rate if required (speed control + dampers). | Airflow too high can displace fibre line; airflow too low may not protect from particulates. |  | 2026-04-04 | 1009 | 1009 | 93 | Pre-filter element; Pre-filter seal/gasket; IPA wipes / cleaning cloth | Per-Draw/Startup | 0 | 20 | 249 | 249 | 1009
Clean Air System (HEPA + Pre-filter + Fan Cabinet) | CAS-MNT-002 | When switching on: confirm fibre position in bare fibre gauge window stays centered; correct if needed | run | 1 | when fan comes on line | Switching – checks during fan start | event |  |  |  | Clean Air System (SG Controls) | Clean Air System.pdf | 4 | When the system is operating and the fan comes on line, verify fibre position in the bare fibre diameter gauge does not move too close to the edge of the measurement window. If it does: exit auto diameter control, correct with joystick, and re-check clean air velocity. Also confirm bare fibre tension is correct and fan start line speed is not too low. | Incorrect clean-air setting can cause fibre displacement and potential contacts (top disc / cooling tubes). |  | 2026-04-04 | 1009 | 1009 | 93 | Pre-filter element; Pre-filter seal/gasket; IPA wipes / cleaning cloth | Routine | 0 | 20 | 249 | 249 | 1009
Clean Air System (HEPA + Pre-filter + Fan Cabinet) | CAS-MNT-003 | Monthly: inspect wear/damage, verify intakes clear, verify airflow uniform & at optimum; balance dampers | calendar | 1 | months | Maintenance – Routine Monthly | calendar |  | months | 7 | Clean Air System (SG Controls) | Clean Air System.pdf | 5 | 1) Visually inspect system for wear/damage. 2) Ensure air intakes are not obstructed; environment not excessively dusty. 3) Using a hand-held anemometer, verify HEPA airflow at fibre line is at optimum setting and consistent between panels and along panel length. 4) Adjust flow using pre-filter cabinet speed control and manifold dampers to balance flows. 5) If correct flow cannot be obtained via speed control, inspect pre-filter and ensure cabinet intake not blocked. | Service frequency may vary based on usage, intake cleanliness, volume of air, and working environment. |  | 2026-03-08 |  | 0 |  | Pre-filter element; Pre-filter seal/gasket; IPA wipes / cleaning cloth | Monthly | 1 | 20
Clean Air System (HEPA + Pre-filter + Fan Cabinet) | CAS-MNT-004 | Every 6 months: replace pre-filter; re-adjust speed control; replace HEPA if airflow remains incorrect | calendar | 6 | months | Maintenance – Routine 6 Monthly | calendar |  | months | 7 | Clean Air System (SG Controls) | Clean Air System.pdf | 6 | 1) Replace pre-filter. 2) Reset speed control to give correct HEPA flow rate. 3) If airflow remains incorrect, replace the HEPA filter. Note: after changing any air filter, speed control must be adjusted to achieve required HEPA flow. | Isolate electrical power before removing/installing/servicing filters. |  | 2025-10-09 |  | 0 |  | Pre-filter element; Pre-filter seal/gasket; HEPA filter element; HEPA gasket/seal; IPA wipes / cleaning cloth | 6-Month | 6 | 45
Clean Air System (HEPA + Pre-filter + Fan Cabinet) | CAS-MNT-005 | As needed: replace pre-filter element (with seal inspection and correct airflow direction) | conditional | 1 | when pre-filter clogged / airflow low | Air Filter Replacement – Pre-filter procedure | event |  |  |  | Clean Air System (SG Controls) | Clean Air System.pdf | 6 | Isolate power. Release cabinet latches, remove outlet to access pre-filter. Remove securing frame and filter element. Inspect PVC foam seals for damage/security. Discard filter, install replacement and securing frame. Ensure filter installed in correct airflow direction (arrows): loose weave faces fan, tight weave faces outlet. Reinstall outlet and close latches; readjust speed control to restore required HEPA flow. | Ensure electrical power is isolated before servicing. |  | 2026-04-04 | 1009 | 1009 | 93 | Pre-filter element; Pre-filter seal/gasket; HEPA filter element; HEPA gasket/seal; IPA wipes / cleaning cloth | On-Condition | 0 | 45 | 249 | 249 | 1009
Clean Air System (HEPA + Pre-filter + Fan Cabinet) | CAS-MNT-006 | As needed: replace HEPA filter element (front face access; tighten nuts diagonally) | conditional | 1 | when airflow incorrect after pre-filter / scheduled change | Air Filter Replacement – HEPA procedure | event |  |  |  | Clean Air System (SG Controls) | Clean Air System.pdf | 7 | Isolate power to pre-filter cabinet. From lift/platform, remove securing nuts from retaining clamps while supporting filter. Lift filter forward, install replacement on supporting rail, refit retaining clamps, hand tighten nuts, then fully tighten nuts in diagonal sequence. After filter change, adjust speed control to achieve required HEPA flow. | Working at height: use guard rails/harness; prevent items falling. Isolate electrical power before servicing. |  | 2026-04-04 | 1009 | 1009 | 93 | Pre-filter element; Pre-filter seal/gasket; HEPA filter element; HEPA gasket/seal; IPA wipes / cleaning cloth | On-Condition | 0 | 45 | 249 | 249 | 1009